|  | ......................... pcs. .............................. € .............................. € GEZE electric spindle drive E 250 NT with IQ box KNX for connection to the KNX building bus For intelligent natural ventilation and use with vertically installed bottom-hung, top-hung and side-hung leaves, inward and outward opening, as well as for skylights and roof windows. Electric spindle drive E 250 NT in 24 V version. The drive must be controlled via a micro-processor. A distinction can be made between alarm and ventilation operating speed. Stroke arresting device and ventilation speed can be programmed as required via software. Overload cut-off and end-position cut-off must be implemented electronically. Sealing via electronically defined pressure. Synchronised multiple operation of up to 3 drives must be guaranteed without additional external module. Activation and setting of the synchro function is by means of an integrated DIP switch without additional programming being necessary. Integration into the KNX bus system via the IQ box KNX. Technical data: Stroke in mm: 100/150/200/230/300/500/750/1000* Tensile force and pressure: 750 N/750 N Voltage: 24 V DC / 230 V AC with external power supply Current consumption: Ventilation (24 V) 0.9 A With stroke 500: 1.1 A IP rating: IP 65 Ambient temperature: -5 °C to +70 °C Power supply cable: 2 m, silicon sheathed* * Special lengths on request Version: ( ) Solo (permissible leaf weight max. 100 kg) ( ) Synchro (permissible leaf weight max. 200 kg) Type of window: ( ) Bottom-hung leaf ( ) Top-hung leaf ( ) Side-hung leaf ( ) Roof window ( ) inward opening ( ) outward opening Leaf dimensions: ......... mm width ......... mm height Leaf material: ( ) Wood ( ) Aluminium ( ) PVC Opening width: ........ mm or max. ....... mm (to be completed by the bidder) Colour: ( ) EV1 ( ) white RAL 9016 ( ) according to RAL .......... |
| --- | --- |
|  | ......................... pcs. .............................. € .............................. € ( ) Standard console for the main closing edge ( ) Inward-opening console for the main closing edge ( ) Swivelling console for the secondary closing edge |
|  | ......................... pcs. .............................. € .............................. € ( ) Safety scissors (2 pcs.) |
|  | ......................... pcs. .............................. € .............................. € ( ) Locking drive Power lock |
|  | ......................... pcs. .............................. € .............................. € IQ box KNX for connecting the spindle drive E 250 NT to the KNX building system for natural ventilation (X) IQ box KNX UP (flush-mounted housing) ( ) IQ box KNX HS (housing fitted to top hat rail) |
|  | ......................... pcs. .............................. € .............................. € Note: You also require a 24 V power supply to supply the window drives as well as the IQ box KNX. |
|  | ......................... pcs. .............................. € .............................. € ( ) Flush-mounted power supply ( ) Power supply fitted to top hat rail |
|  | ......................... pcs. .............................. € .............................. € Installation and functional test Installation and functional test by an expert authorised by the manufacturer. |
|  | ......................... pcs. .............................. € .............................. € Start-up and official approval Official approval of the complete smoke and heat extraction system by an officially recognised expert, who also hands over the acceptance certificates. |
|  | ......................... pcs. .............................. € .............................. € Service maintenance - compact package Maintenance and testing of hold-open systems (optional position) Service package for maintenance and testing according to ASR A1.7 as well as according to manufacturer’s specification with the following performance features: - One maintenance per contract year - Free provision and updating of the test documents - Attachment of the inspection sticker - Fault diagnosis and repair jobs during the contract period will be carried out at reduced hourly rates - Service technicians will be deployed within 24 hours of the message being received from Monday – Friday between 7 am and 5 pm without surcharges - Personal availability at the help desk 24 hours a day, 365 days a year - Contract run time: 2 years |
|  | ......................... pcs. .............................. € .............................. € Service maintenance - comfort package Service maintenance (optional position) Comfort service package for maintenance and accident prevention inspection in accordance with ASR A1.7 as well as according to manufacturer’s specification with the following performance features: - Extension of the warranty to 36 months (condition: the maintenance contract is concluded 3 months after the commissioning date at the latest) - One maintenance per contract year - Free provision and updating of the test documents - Attachment of the inspection sticker - No separate charging for services and travel costs during the warranty period - No separate charging for consumables up to € 25 per maintenance - No separate charging for working hours when spare parts are replaced during the maintenance - Personal availability at the help desk 24 hours a day, 365 days a year - Contract run time: 3 years |
|  | ......................... pcs. .............................. € .............................. € Delivery and installation Wiring to be carried out on site by an electrical contractor according to the GEZE cable plan. Delivery, installation and commissioning through plant fitters or service partner. Safety analysis, instruction of the operator as to how the system works and handing over of the documentation. Annual maintenance and technical inspection by an expert authorised by the manufacturer incl. documentation of the inspection in an inspection log. |